## Slide 1: TOCP Rack-Level Architecture
Matt St Peter

## Slide 2: General OCP Characteristics
Custom Rack:
  Wider aperture (21” vs 17.1”), different “U” (48mm vs 44.5mm)
Custom Power Distribution:
  Three vertical 12V high-current power rails
  Power GND tied to logic GND
Custom Sled and Shelf:
  Three sleds across the rack width
  Open sled design, very simple cooling, no EMC control
Front Cabling, No Cabling Plan:
  Optical and copper cables connect from front of sleds to ToR switch
No Management Plan:
  Resisting IPMI, simple concept

## Slide 3: Benefits of our approach
Standard Rack and Rack-Level Components:
  Can be mix-and-match, depending on application.
High Density:
  Two server PCBAs per 2U sled, support for future high-capacity DRAM.
Performance:
  Scaling from high-end to low-end, with equal or better performance
In-Band Management:
  Simplified hardware integration, cabling
  Improved sled manageability with additional features
Storage Option:
  Multiple drive storage architecture
Automatic Cabling:
  Rear cabling with blind-mate sled connections

## Slide 4: Major Rack-Level Sections
Rack Infrastructure
    Rack HW, base, panels, top
    Network Connections between sleds and ToRs
Power Entry, Conversion, and Distribution
  Power feed options (AC/DC, voltage, isolation)
  Rear power rails with attachment to standard 19” rack
  Power management
ToR Load-Balancing Switch
  Mounting, power, datapath and management connections
CPU Sled and Shelf Design
  Power and network blind-mate connections
  Sled enclosure, mounting, alignment, and retention
  PCBA mounting, HDD/SSD mounting, external I/O, EMC control
  Transition board, internal cabling
  Internal fans and airflow

## Slide 5: TOCP System-Level

## Slide 6: Rack-Level Overall View
Zone 1
Zone 2
Zone 3
2U Unused
Standard 44U 19” rack
Features:
Zone Independence:
  Power
  Dataplane
  Management
  Airflow and cooling
Selectable Zone Count
  1 through 4
Field upgradable
  Sleds (performance, power, features)
  ToR (capacity, features)
  Power (capacity)
Local Failure Domains
Use of industry standard parts
Simplicity
Low cost

## Slide 7: General Rack Configuration
ToR-LB
ToR-LB
Front View
Side View
Sled#1a
Sled#1b
Sled#2a
Sled#2b
Sled#3a
Sled#3b
Sled#4a
Sled#4b
Sled#5a
Sled#5b
Sled#6a
Sled#6b
Sled#7a
Sled#7b
Sled#8a
Sled#8b
Sled#9a
Sled#9b
Sled#10a
Sled#10b
Sled#11a
Sled#11b
Sled#12a
Sled#12b
Sled#13a
Sled#13b
Sled#14a
Sled#14b
Sled#15a
Sled#15b
Sled#16a
Sled#16b
Uplink Ports
Front
Rear
16 trays
32 sleds
64 processors
Up to 40G to each sled
ToR-LB
ToR-LB
Uplink Ports
CPU sled, 2U height, 2 sleds per shelf
PSU, 4-bay, 1-2U height, 1 per zone
ToR, 2U height, 1 per zone, 8x 100Gb uplinks
Optical fibers, 4 pairs per 2U side, 32 sets of 4 pairs per rack

## Slide 8: Rack-Level Detail View
Number of zones is variable
  Independent power, data, management, cooling

## Slide 9: TOCP Sled Configuration Options
1U CPU PCBA
1U sled, 4 Reduced Perf Dual-CPU PBAs per 2U, 40mm fans
1U CPU PCBA
1U CPU PCBA
1U CPU PCBA
2U CPU PCBA
2U CPU PCBA
1U CPU PCBA
1U CPU PCBA
1U CPU PCBA
1U CPU PCBA
2U sled, 2 High-Perf Dual-CPU PBAs per 2U, 80mm fans
2U sled, 4 Mid-Perf Dual-CPU PBAs per 2U, 80mm fans
Shelf
Sled

## Slide 10: Sled Height Options
1U SLED implementation/1U Mechanical Implementation
  Greater compute node density (2X) vs. 2U (assuming dual socket)
  4x 40mm fans required per tray, based on tray width
  Shorter heat sinks (for 1U) will limit high-end CPU SKUs
  1x3.5” HDD per sled
  Lower sled Network throughput requirement (1x10Gb or 1x40Gb)
  Does not allow for Storage Sled
Hybrid (2x “1U” PBA, 2U mechanical enclosure)
  Same compute node density, heatsinks as 1U SLED
  2x 80mm fans per 2U tray
  Multiple 3.5” HDD in Storage Sled
  Higher throughput requirement (2x10Gb or 2x 40Gb)
  Storage Sled can be one PCBA and multiple HDD

## Slide 11: Rack-Level Zone 1 of 3 Detail View
Top-of-Rack can support up to 32 sleds
Up to 10 sleds per Zone (total 3 Zones)
Each Sled is made up of two Dual-Socket Servers (CPU Sled) or one on Storage Sleds
Local Zone AC-DC power conversion

## Slide 12: Sled-Level Front and Side View
Each Sled has one or two Server PCBAs in an overall 2U height
Two Sleds share control of the local fans. If one server fails, the other takes over.
Each Compute Sled may have local boot drives. Additionally, a Storage Sled has a single Server PCBA and several rotating Drives, based on required capacity.
All Sled Power and Data interfaces automatically connect when a Sled is installed in the Shelf.
Right half of Shelf shown (one Sled)

## Slide 13: Zone-Level Power Feed Detail
Wired DC Power Feed To ToR
Local Zone Power Rails
N+1 Redundand Modular AC-DC Conversion

## Slide 14: Zone-Level Data/Management Detail
Dataplane Uplinks (Up to 16 per ToR)
Downlinks to Individual Sleds (2 per sled)
Management Uplinks (2 per ToR)

## Slide 15: Tray vs. rack-level cooling
 | Tray Level | Shelf / Rack Level
Tray independence | Each trays completely independent of surrounding trays | Inter-tray dependencies for air flow & impedance fan control power budget
Management | Flat management hierarchy, no shelf/rack level layer required Simple integrated management controllers suffice | Additional layer of management required with shared controls, power & thermal budgeting BMC & ShMC required
Fans & Acoustics | Medium-size 80mm fans, much lower noise than 40mm Fans are inside sled housing | 80mm (larger size might not work) Additional shelf/rack air plenum space needed for airflow
Serviceability | Trays independently front serviceable | Rear access required, tray service impact, cost & complexity Competition with rear I/O & power rails for panel space & access
Availability | Failures localized to one tray | Fan failure impacts multiple trays
Cost & Complexity | KISS | Inter-tray dependencies, management hierarchy

## Slide 16: Rack Images

## Slide 17: Rack-Level Rear View
Each Sled has two 80mm fans providing local airflow as needed by the local processors.
Fan capacity scales with the Sled type and performance.
Two Servers direct the fan speed based on their own needs, the fans run at the higher of the two settings.

## Slide 18: Sled Level Rear View

## Slide 19: Rear Optical Interconnects
  Up to 4x 2x 4 Lanes per connector with Molex HBMT
  (Connect to 8 sites)
Notes: SFP/SFP+ width = 15mm
QSFP/zQSFP+ width = 19mm

## Slide 20: TOCP ToR, Gen1, 3U Physicals

## Slide 21: TOCP ToR, Gen2, 2U Physicals

## Slide 22: Rack-Level Power Requirements
Rack Power Feed:
  DC option, -48V
  AC option, two or three phase
  Not clearly defined
Sled:
  Direct 12V feed from vertical power rail
  One 12V feed per sled (non-redundant)
Gen1 ToR:
  Based on Schroff 3U 2-Slot F-B DC chassis
  Cabled -48V power feed from AC/DC power shelf (may be redundant)
Gen2 ToR:
  Custom design
  Expected to be 2U
  Direct 12V feed from two vertical power rails (redundant option)

## Slide 23: Sled Components

## Slide 24: CPU Sled-Level Connections

## Slide 25: Storage Sled-Level Connections

## Slide 26: Sled Level Top View

## Slide 27: Supermicro X10DRFR Server Board
Features:
Set up for 1U enclosure height
Rear I/O Setup
Support for up to 16 DIMMS
Site for Plug-In I/O card

## Slide 28: Supermicro AOC-CTG-i1S
1. Intel 82599EN 10GbE Controller
2. Single SFP+ Port
3. Dual USB 2.0 Ports

## Slide 29: Supermicro AOC-CTG-i2S
1. Intel 82599ES 10GbE Controller
2. Dual SFP+ Port
3. Dual USB 2.0 Ports

## Slide 30: AOC-CTG-i1(2)S Support Bracket (1U)
AOC-CTG-i2S Add-In card with BKT-0061L installed

## Slide 31: Work Going Forward

## Slide 32: Schroff Work Areas – Summary
Sled Mechanical Design:
  External dimensions, slide design, overall fit
  Internal fit, eject mechanism
  Storage mounting for SSD and HDD
Sled Electrical Design:
  Rear interface card design
  HDD interface card design
  General cable fit
Power Conversion and Distribution:
  AC/DC input to 12V conversion shelf for power rail
  AC/DC input to -48V conversion shelf for Gen1 ToR
  Internal power cabling
General Rack Mechanics:
  Rack components and standards

## Slide 33: Schroff Work Areas – Sled Mechanics
Overall Dimensions:
  Define front and rear cable space allowance, including front optics
  Width and height defined by shelf-sled mechanical interface
  Define all tolerances to cover power and optical blind-mate connectors
  Airflow and cooling design and test
Internal Component Fit:
  Front 2.5” SSD with mounting
  Exhaust fan and rear interface card positions
  Main PCBA
Front Lock-Eject Lever:
  Non-electrical (no eject switch)
  One 12V feed per sled (non-redundant)
Storage Version HDD Mounting:
  Up to five drives, install from left side
  Receiver and hold-down concept
  Interface card for power, LED, presence, and data

## Slide 34: Schroff Work Areas – Sled Electricals
Power and Fan Interface Card:
  12V high-current conducted noise filtering
  DC hot-swap and soft-start interlock, fusing
  Limited power control with 5V-SBY
  Limited I2C support
  Fan PWM and tachometer merge
Power Interlock:
  Simple method, similar to ATCA hot-swap/soft-start
HDD Interface Card:
  5V and 12V pass-through
  Presence and LED signals
  SATA signals

## Slide 35: Sled Hot-Swap Support
Safe Connect/Disconnect to 12VRails:
  Mechanical detect of full install with electrical shut-off
Operator BMC Interface:
  Front Hot-Swap button
  Hot-Swap status LED
  Same concept as ATCA fan module

## Slide 36: End